## Sheet1
Modbus App
| Modbus address (dec) | Modbus address (hex) | Read coils | Read holding registers | Read input registers (0x06) | Write single coil (0x05) | Write single register (0x06) | Write multiple registers (0x10) | Description | Access | Data type | Data length in bytes | Number of registers | Data | Example
Modbus | 0 | 0000 | [13 empty] | 0 - 1000 (Modbus Interface)
Interface | 1 | 0001 |  |  | x |  |  |  | Modbus Ver | R | uint(16) | 2 | 1
| 2 | 0002 |  |  | x |  |  |  | Modbus Info | R | uint(16) | 2 | 1
Measurements | 1000 | 03E8 |  |  | x |  |  |  | Frequency | R | float | 4 | 2 | Floating point number IEEE754 | 60 | 1000 - 3000 (Measurements)
| 1002 | 03EA |  |  | x |  |  |  | Output A frequency | R | float | 4 | 2 | Floating point number IEEE754
| 1004 | 03EC |  |  | x |  |  |  | Output B frequency | R | float | 4 | 2 | Floating point number IEEE754
| 1006 | 03EE |  |  | x |  |  |  | Output C frequency | R | float | 4 | 2 | Floating point number IEEE754
| 1008 | 03F0 |  |  | x |  |  |  | Voltage line to line ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1010 | 03F2 |  |  | x |  |  |  | Output A voltage line to line ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1012 | 03F4 |  |  | x |  |  |  | Output B voltage line to line ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1014 | 03F6 |  |  | x |  |  |  | Output C voltage line to line ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1016 | 03F8 |  |  | x |  |  |  | Voltage line to line AC | R | float | 4 | 2 | Floating point number IEEE754
| 1018 | 03FA |  |  | x |  |  |  | Output A voltage line to line AC | R | float | 4 | 2 | Floating point number IEEE754
| 1020 | 03FC |  |  | x |  |  |  | Output B voltage line to line AC | R | float | 4 | 2 | Floating point number IEEE754
| 1022 | 03FE |  |  | x |  |  |  | Output C voltage line to line AC | R | float | 4 | 2 | Floating point number IEEE754
| 1024 | 0400 |  |  | x |  |  |  | Voltage line to line DC | R | float | 4 | 2 | Floating point number IEEE754
| 1026 | 0402 |  |  | x |  |  |  | Output A voltage line to line DC | R | float | 4 | 2 | Floating point number IEEE754
| 1028 | 0404 |  |  | x |  |  |  | Output B voltage line to line DC | R | float | 4 | 2 | Floating point number IEEE754
| 1030 | 0406 |  |  | x |  |  |  | Output C voltage line to line DC | R | float | 4 | 2 | Floating point number IEEE754
| 1032 | 0408 |  |  | x |  |  |  | Voltage ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1034 | 040A |  |  | x |  |  |  | Output A voltage ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1036 | 040C |  |  | x |  |  |  | Output B voltage ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1038 | 040E |  |  | x |  |  |  | Output C voltage ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1040 | 0410 |  |  | x |  |  |  | Voltage AC | R | float | 4 | 2 | Floating point number IEEE754
| 1042 | 0412 |  |  | x |  |  |  | Output A voltage AC | R | float | 4 | 2 | Floating point number IEEE754
| 1044 | 0414 |  |  | x |  |  |  | Output B voltage AC | R | float | 4 | 2 | Floating point number IEEE754
| 1046 | 0416 |  |  | x |  |  |  | Output C voltage AC | R | float | 4 | 2 | Floating point number IEEE754
| 1048 | 0418 |  |  | x |  |  |  | Voltage DC | R | float | 4 | 2 | Floating point number IEEE754
| 1050 | 041A |  |  | x |  |  |  | Output A voltage DC | R | float | 4 | 2 | Floating point number IEEE754
| 1052 | 041C |  |  | x |  |  |  | Output B voltage DC | R | float | 4 | 2 | Floating point number IEEE754
| 1054 | 041E |  |  | x |  |  |  | Output C voltage DC | R | float | 4 | 2 | Floating point number IEEE754
| 1056 | 0420 |  |  | x |  |  |  | Current ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1058 | 0422 |  |  | x |  |  |  | Output A current ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1060 | 0424 |  |  | x |  |  |  | Output B current ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1062 | 0426 |  |  | x |  |  |  | Output C current ACDC | R | float | 4 | 2 | Floating point number IEEE754
| 1064 | 0428 |  |  | x |  |  |  | Current DC | R | float | 4 | 2 | Floating point number IEEE754
| 1066 | 042A |  |  | x |  |  |  | Output A current DC | R | float | 4 | 2 | Floating point number IEEE754
| 1068 | 042C |  |  | x |  |  |  | Output B current DC | R | float | 4 | 2 | Floating point number IEEE754
| 1070 | 042E |  |  | x |  |  |  | Output C current DC | R | float | 4 | 2 | Floating point number IEEE754
| 1072 | 0430 |  |  | x |  |  |  | Active power | R | float | 4 | 2 | Floating point number IEEE754
| 1074 | 0432 |  |  | x |  |  |  | Output A active power | R | float | 4 | 2 | Floating point number IEEE754
| 1076 | 0434 |  |  | x |  |  |  | Output B active power | R | float | 4 | 2 | Floating point number IEEE754
| 1078 | 0436 |  |  | x |  |  |  | Output C active power | R | float | 4 | 2 | Floating point number IEEE754
| 1080 | 0438 |  |  | x |  |  |  | Apparent power | R | float | 4 | 2 | Floating point number IEEE754
| 1082 | 043A |  |  | x |  |  |  | Output A apparent power | R | float | 4 | 2 | Floating point number IEEE754
| 1084 | 043C |  |  | x |  |  |  | Output B apparent power | R | float | 4 | 2 | Floating point number IEEE754
| 1086 | 043E |  |  | x |  |  |  | Output C apparent power | R | float | 4 | 2 | Floating point number IEEE754
| 1088 | 0440 |  |  | x |  |  |  | Peak current | R | float | 4 | 2 | Floating point number IEEE754
| 1090 | 0442 |  |  | x |  |  |  | Output A peak current | R | float | 4 | 2 | Floating point number IEEE754
| 1092 | 0444 |  |  | x |  |  |  | Output B peak current | R | float | 4 | 2 | Floating point number IEEE754
| 1094 | 0446 |  |  | x |  |  |  | Output C peak current | R | float | 4 | 2 | Floating point number IEEE754
| 1096 | 0448 |  |  | x |  |  |  | Power factor | R | float | 4 | 2 | Floating point number IEEE754
| 1098 | 044A |  |  | x |  |  |  | Output A power factor | R | float | 4 | 2 | Floating point number IEEE754
| 1100 | 044C |  |  | x |  |  |  | Output B power factor | R | float | 4 | 2 | Floating point number IEEE754
| 1102 | 044E |  |  | x |  |  |  | Output C power factor | R | float | 4 | 2 | Floating point number IEEE754
| 1104 | 0450 |  |  | x |  |  |  | Crest factor | R | float | 4 | 2 | Floating point number IEEE754
| 1106 | 0452 |  |  | x |  |  |  | Output A crest factor | R | float | 4 | 2 | Floating point number IEEE754
| 1108 | 0454 |  |  | x |  |  |  | Output B crest factor | R | float | 4 | 2 | Floating point number IEEE754
| 1110 | 0456 |  |  | x |  |  |  | Output C crest factor | R | float | 4 | 2 | Floating point number IEEE754
| 1112 | 0458 |  |  | x |  |  |  | Peak current recorded | R | float | 4 | 2 | Floating point number IEEE754
| 1114 | 045A |  |  | x |  |  |  | Output A peak current recorded | R | float | 4 | 2 | Floating point number IEEE754
| 1116 | 045C |  |  | x |  |  |  | Output B peak current recorded | R | float | 4 | 2 | Floating point number IEEE754
| 1118 | 045E |  |  | x |  |  |  | Output C peak current recorded | R | float | 4 | 2 | Floating point number IEEE754
| 1120 | 0460 |  |  | x |  |  |  | Voltage thd | R | float | 4 | 2 | Floating point number IEEE754
| 1122 | 0462 |  |  | x |  |  |  | Output A voltage thd | R | float | 4 | 2 | Floating point number IEEE754
| 1124 | 0464 |  |  | x |  |  |  | Output B voltage thd | R | float | 4 | 2 | Floating point number IEEE754
| 1126 | 0466 |  |  | x |  |  |  | Output C voltage thd | R | float | 4 | 2 | Floating point number IEEE754
| 1128 | 0468 |  |  | x |  |  |  | Current thd | R | float | 4 | 2 | Floating point number IEEE754
| 1130 | 046A |  |  | x |  |  |  | Output A current thd | R | float | 4 | 2 | Floating point number IEEE754
| 1132 | 046C |  |  | x |  |  |  | Output B current thd | R | float | 4 | 2 | Floating point number IEEE754
| 1134 | 046E |  |  | x |  |  |  | Output C current thd | R | float | 4 | 2 | Floating point number IEEE754
| 1136 | 0470 |  |  | x |  |  |  | Power factor angle | R | float | 4 | 2 | Floating point number IEEE754
| 1138 | 0472 |  |  | x |  |  |  | Output A power factor angle | R | float | 4 | 2 | Floating point number IEEE754
| 1140 | 0474 |  |  | x |  |  |  | Output B power factor angle | R | float | 4 | 2 | Floating point number IEEE754
| 1142 | 0476 |  |  | x |  |  |  | Output C power factor angle | R | float | 4 | 2 | Floating point number IEEE754
| 1144 | 0478 |  |  | x |  |  |  | Displacement factor | R | float | 4 | 2 | Floating point number IEEE754
| 1146 | 047A |  |  | x |  |  |  | Output A displacement factor | R | float | 4 | 2 | Floating point number IEEE754
| 1148 | 047C |  |  | x |  |  |  | Output B displacement factor | R | float | 4 | 2 | Floating point number IEEE754
| 1150 | 047E |  |  | x |  |  |  | Output C displacement factor | R | float | 4 | 2 | Floating point number IEEE754
| 1152 | 0480 |  |  | x |  |  |  | Distortion factor | R | float | 4 | 2 | Floating point number IEEE754
| 1154 | 0482 |  |  | x |  |  |  | Output A distortion factor | R | float | 4 | 2 | Floating point number IEEE754
| 1156 | 0484 |  |  | x |  |  |  | Output B distortion factor | R | float | 4 | 2 | Floating point number IEEE754
| 1158 | 0486 |  |  | x |  |  |  | Output C distortion factor | R | float | 4 | 2 | Floating point number IEEE754
| 1160 | 0488 |  |  | x |  |  |  | Kilowatt hour | R | float | 4 | 2 | Floating point number IEEE754
| 1162 | 048A |  |  | x |  |  |  | Output A kilowatt hour | R | float | 4 | 2 | Floating point number IEEE754
| 1164 | 048C |  |  | x |  |  |  | Output B kilowatt hour | R | float | 4 | 2 | Floating point number IEEE754
| 1166 | 048E |  |  | x |  |  |  | Output C kilowatt hour | R | float | 4 | 2 | Floating point number IEEE754
| 1168 | 0490 |  |  | x |  |  |  | Kilowatt hour elapsed time | R | float | 4 | 2 | Floating point number IEEE754
| 1170 | 0492 |  |  | x |  |  |  | Output A kilowatt hour elapsed time | R | float | 4 | 2 | Floating point number IEEE754
| 1172 | 0494 |  |  | x |  |  |  | Output B kilowatt hour elapsed time | R | float | 4 | 2 | Floating point number IEEE754
| 1174 | 0496 |  |  | x |  |  |  | Output C kilowatt hour elapsed time | R | float | 4 | 2 | Floating point number IEEE754
| 2800 | 0AF0 | x |  |  | x |  |  | Reset KWH | RW | bool |  |  | Coils : Kreset | ON=reset, self clear
| 2801 | 0AF1 | x |  |  | x |  |  | Enable KWH | RW | bool |  |  | Coils : Kwhenable | ON=enable, OFF=disable
Setpoints | 3000 | 0BB8 | [6 empty] | Program frequency | RW | float | 4 | 2 | Floating point number IEEE754 |  | 3000 - 5000 (Setpoints)
Program | 3002 | 0BBA | [6 empty] | Program frequency A | RW | float | 4 | 2 | Floating point number IEEE754
| 3004 | 0BBC | [6 empty] | Program frequency B | RW | float | 4 | 2 | Floating point number IEEE754
| 3006 | 0BBE | [6 empty] | Program frequency C | RW | float | 4 | 2 | Floating point number IEEE754
| 3008 | 0BC0 | [6 empty] | Program voltage AC | RW | float | 4 | 2 | Floating point number IEEE754 | Value=VALUE if all set, Value=0 if else
| 3010 | 0BC2 | [6 empty] | Program voltage AC output A | RW | float | 4 | 2 | Floating point number IEEE754
| 3012 | 0BC4 | [6 empty] | Program voltage AC output B | RW | float | 4 | 2 | Floating point number IEEE754
| 3014 | 0BC6 | [6 empty] | Program voltage AC output C | RW | float | 4 | 2 | Floating point number IEEE754
| 3016 | 0BC8 | [6 empty] | Program voltage DC | RW | float | 4 | 2 | Floating point number IEEE754 | Value=VALUE if all set, Value=0 if else
| 3018 | 0BCA | [6 empty] | Program voltage DC output A | RW | float | 4 | 2 | Floating point number IEEE754
| 3020 | 0BCC | [6 empty] | Program voltage DC output B | RW | float | 4 | 2 | Floating point number IEEE754
| 3022 | 0BCE | [6 empty] | Program voltage DC output C | RW | float | 4 | 2 | Floating point number IEEE754
| 3024 | 0BD0 | [6 empty] | Power limit | RW | float | 4 | 2 | Floating point number IEEE754 | Value=VALUE if all set, Value=0 if else
| 3026 | 0BD2 | [6 empty] | Power limit output A | RW | float | 4 | 2 | Floating point number IEEE754
| 3028 | 0BD4 | [6 empty] | Power limit output B | RW | float | 4 | 2 | Floating point number IEEE754
| 3030 | 0BD6 | [6 empty] | Power limit output C | RW | float | 4 | 2 | Floating point number IEEE754
| 3032 | 0BD8 | [6 empty] | Current limit ABC | RW | float | 4 | 2 | Floating point number IEEE754 | Value=VALUE if all set, Value=0 if else
| 3034 | 0BDA | [6 empty] | Current limit output A | RW | float | 4 | 2 | Floating point number IEEE754
| 3036 | 0BDC | [6 empty] | Current limit output B | RW | float | 4 | 2 | Floating point number IEEE754
| 3038 | 0BDE | [6 empty] | Current limit output C | RW | float | 4 | 2 | Floating point number IEEE754
| 3040 | 0BE0 | [6 empty] | KVA Limit | RW | float | 4 | 2 | Floating point number IEEE754 | Value=VALUE if all set, Value=0 if else
| 3042 | 0BE2 | [6 empty] | KVA Limit output A | RW | float | 4 | 2 | Floating point number IEEE754
| 3044 | 0BE4 | [6 empty] | KVA Limit output B | RW | float | 4 | 2 | Floating point number IEEE754
| 3046 | 0BE6 | [6 empty] | KVA Limit output C | RW | float | 4 | 2 | Floating point number IEEE754
| 3048 | 0BE8 | [6 empty] | Phase offset output B | RW | float | 4 | 2 | Floating point number IEEE754
| 3050 | 0BEA | [6 empty] | Phase offset output C | RW | float | 4 | 2 | Floating point number IEEE754
| 4000 | 0FA0 | x |  |  | x |  |  | Enable output | RW | bool |  |  | Coils: Output | ON=enable, OFF=disable
| 4001 | 0FA1 | x |  |  | x |  |  | Enable output A | RW | bool |  |  | Coils: Output | ON=enable, OFF=disable
| 4002 | 0FA2 | x |  |  | x |  |  | Enable output B | RW | bool |  |  | Coils: Output | ON=enable, OFF=disable
| 4003 | 0FA3 | x |  |  | x |  |  | Enable output C | RW | bool |  |  | Coils: Output | ON=enable, OFF=disable
Protection | 5000 | 1388 | x |  |  | x |  |  | RMS Current protection | RW | bool |  |  |  |  | 5000 - 6000 (Protection)
| 5001 | 1389 | x |  |  | x |  |  | Output A RMS Current protection | RW | bool
| 5002 | 138A | x |  |  | x |  |  | Output B RMS Current protection | RW | bool
| 5003 | 138B | x |  |  | x |  |  | Output C RMS Current protection | RW | bool
| 5004 | 138C | x |  |  | x |  |  | RMS Power protection | RW | bool
| 5005 | 138D | x |  |  | x |  |  | Output A RMS Power protection | RW | bool
| 5006 | 138E | x |  |  | x |  |  | Output B RMS Power protection | RW | bool
| 5007 | 138F | x |  |  | x |  |  | Output C RMS Power protection | RW | bool
| 5008 | 1390 | x |  |  | x |  |  | Peak current protection | RW | bool
| 5009 | 1391 | x |  |  | x |  |  | Output A Peak current protection | RW | bool
| 5010 | 1392 | x |  |  | x |  |  | Output B Peak current protection | RW | bool
| 5011 | 1393 | x |  |  | x |  |  | Output C Peak current protection | RW | bool
| 5012 | 1394 | x |  |  | x |  |  | Peak voltage protection | RW | bool
| 5013 | 1395 | x |  |  | x |  |  | Output A Peak voltage protection | RW | bool
| 5014 | 1396 | x |  |  | x |  |  | Output B Peak voltage protection | RW | bool
| 5015 | 1397 | x |  |  | x |  |  | Output C Peak voltage protection | RW | bool
| 5024 | 13A0 | [6 empty] | Current level | RW | float | 4 | 2 | Floating point number IEEE754
| 5026 | 13A2 | [6 empty] | Output A Current level | RW | float | 4 | 2 | Floating point number IEEE754
| 5028 | 13A4 | [6 empty] | Output B Current level | RW | float | 4 | 2 | Floating point number IEEE754
| 5030 | 13A6 | [6 empty] | Output C Current level | RW | float | 4 | 2 | Floating point number IEEE754
| 5032 | 13A8 | [6 empty] | Power level | RW | float | 4 | 2 | Floating point number IEEE754
| 5034 | 13AA | [6 empty] | Output A Power level | RW | float | 4 | 2 | Floating point number IEEE754
| 5036 | 13AC | [6 empty] | Output B Power level | RW | float | 4 | 2 | Floating point number IEEE754
| 5038 | 13AE | [6 empty] | Output C Power level | RW | float | 4 | 2 | Floating point number IEEE754
| 5040 | 13B0 | [6 empty] | KVA Level | RW | float | 4 | 2 | Floating point number IEEE754
| 5042 | 13B2 | [6 empty] | Output A KVA Level | RW | float | 4 | 2 | Floating point number IEEE754
| 5044 | 13B4 | [6 empty] | Output B KVA Level | RW | float | 4 | 2 | Floating point number IEEE754
| 5046 | 13B6 | [6 empty] | Output C KVA Level | RW | float | 4 | 2 | Floating point number IEEE754
| 5048 | 13B8 | [6 empty] | Trip time | RW | float | 4 | 2 | Floating point number IEEE754 | minimum step of 0.1 seconds
| 5050 | 13BA | [6 empty] | Output A Trip time | RW | float | 4 | 2 | Floating point number IEEE754
| 5052 | 13BC | [6 empty] | Output B Trip time | RW | float | 4 | 2 | Floating point number IEEE754
| 5054 | 13BE | [6 empty] | Output C Trip time | RW | float | 4 | 2 | Floating point number IEEE754
| 5056 | 13C0 | [6 empty] | Peak current limit | RW | float | 4 | 2 | Floating point number IEEE754
| 5058 | 13C2 | [6 empty] | Output A Peak current limit | RW | float | 4 | 2 | Floating point number IEEE754
| 5060 | 13C4 | [6 empty] | Output B Peak current limit | RW | float | 4 | 2 | Floating point number IEEE754
| 5062 | 13C6 | [6 empty] | Output C Peak current limit | RW | float | 4 | 2 | Floating point number IEEE754
| 5064 | 13C8 | [6 empty] | Peak current protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5066 | 13CA | [6 empty] | Output A Peak current protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5068 | 13CC | [6 empty] | Output B Peak current protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5070 | 13CE | [6 empty] | Output C Peak current protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5072 | 13D0 | [6 empty] | Peak voltage protection margin | RW | float | 4 | 2 | Floating point number IEEE754
| 5074 | 13D2 | [6 empty] | Output A Peak voltage protection margin | RW | float | 4 | 2 | Floating point number IEEE754
| 5076 | 13D4 | [6 empty] | Output B Peak voltage protection margin | RW | float | 4 | 2 | Floating point number IEEE754
| 5078 | 13D6 | [6 empty] | Output C Peak voltage protection margin | RW | float | 4 | 2 | Floating point number IEEE754
| 5080 | 13D8 | [6 empty] | Peak voltage protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5082 | 13DA | [6 empty] | Output A Peak voltage protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5084 | 13DC | [6 empty] | Output B Peak voltage protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5086 | 13DE | [6 empty] | Output C Peak voltage protection level | RW | float | 4 | 2 | Floating point number IEEE754
| 5088 | 13E0 | [6 empty] | Peak voltage protection mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits | 0=MARGIN, 1=LEVEL, 2=MARGIN&LEVEL
| 5090 | 13E2 | [6 empty] | Output A Peak voltage protection mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits
| 5092 | 13E4 | [6 empty] | Output B Peak voltage protection mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits
| 5094 | 13E6 | [6 empty] | Output C Peak voltage protection mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits
Configuration | 6000 | 1770 | [6 empty] | Ramp time | RW | float | 4 | 2 | Floating point number IEEE754 | 0.222 Seconds | 6000 - 7000 (Slew & Ramp)
Slew | 6002 | 1772 | [6 empty] | Output A Ramp time | RW | float | 4 | 2 | Floating point number IEEE754
| 6004 | 1774 | [6 empty] | Output B Ramp time | RW | float | 4 | 2 | Floating point number IEEE754
| 6006 | 1776 | [6 empty] | Output C Ramp time | RW | float | 4 | 2 | Floating point number IEEE754
| 6008 | 1778 | [6 empty] | Voltage AC | RW | float | 4 | 2 | Floating point number IEEE754
| 6010 | 177A | [6 empty] | Output A Voltage AC | RW | float | 4 | 2 | Floating point number IEEE754
| 6012 | 177C | [6 empty] | Output B Voltage AC | RW | float | 4 | 2 | Floating point number IEEE754
| 6014 | 177E | [6 empty] | Output C Voltage AC | RW | float | 4 | 2 | Floating point number IEEE754
| 6016 | 1780 | [6 empty] | Frequency | RW | float | 4 | 2 | Floating point number IEEE754
| 6018 | 1782 | [6 empty] | Output A Frequency | RW | float | 4 | 2 | Floating point number IEEE754
| 6020 | 1784 | [6 empty] | Output B Frequency | RW | float | 4 | 2 | Floating point number IEEE754
| 6022 | 1786 | [6 empty] | Output C Frequency | RW | float | 4 | 2 | Floating point number IEEE754
| 6024 | 1788 | [6 empty] | Voltage DC | RW | float | 4 | 2 | Floating point number IEEE754
| 6026 | 178A | [6 empty] | Output A Voltage DC | RW | float | 4 | 2 | Floating point number IEEE754
| 6028 | 178C | [6 empty] | Output B Voltage DC | RW | float | 4 | 2 | Floating point number IEEE754
| 6030 | 178E | [6 empty] | Output C Voltage DC | RW | float | 4 | 2 | Floating point number IEEE754
| 6032 | 1790 | [6 empty] | Phase | RW | float | 4 | 2 | Floating point number IEEE754
| 6034 | 1792 | [6 empty] | Output A Phase | RW | float | 4 | 2 | Floating point number IEEE754
| 6036 | 1794 | [6 empty] | Output B Phase | RW | float | 4 | 2 | Floating point number IEEE754
| 6038 | 1796 | [6 empty] | Output C Phase | RW | float | 4 | 2 | Floating point number IEEE754
| 6040 | 1798 |  |  |  | x |  |  | Slew rate control | RW | bool
| 6041 | 1799 |  |  |  | x |  |  | Output A Slew rate control | RW | bool
| 6042 | 179A |  |  |  | x |  |  | Output B Slew rate control | RW | bool
| 6043 | 179B |  |  |  | x |  |  | Output C Slew rate control | RW | bool
Configuration | 8000 | 1F40 | [6 empty] | Configuration form | RW | uint(16) | 2 | 1 | unsigned int 16 bits | 1=SINGLE, 2=SPLIT, 3=THREE | 8000 - 9000 (Configuration)
Unit | 8001 | 1F41 | [6 empty] | Configuration voltage range | RW | uint(16) | 2 | 1 | unsigned int 16 bits | 0=LOW, 1=HIGH
Settings | 8002 | 1F42 | [6 empty] | Configuration mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits | 0=AC, 1=DC, 2=AC-DC
| 8003 | 1F43 | [6 empty] | Phase rotation | RW | uint(16) | 2 | 1 | unsigned int 16 bits | 0=NEGATIVE, 1=POSITIVE
| 8004 | 1F44 | [6 empty] | Output impedance mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits | 0=REAL TIME, 1=RMS
| 8005 | 1F45 | [6 empty] | Output A impedance mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits
| 8006 | 1F46 | [6 empty] | Output B impedance mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits
| 8007 | 1F47 | [6 empty] | Output C impedance mode | RW | uint(16) | 2 | 1 | unsigned int 16 bits
| 8016 | 1F50 | [6 empty] | Update phase | RW | float | 4 | 2 | Floating point number IEEE754
| 8018 | 1F52 | [6 empty] | Output A update phase | RW | float | 4 | 2 | Floating point number IEEE754
| 8020 | 1F54 | [6 empty] | Output B update phase | RW | float | 4 | 2 | Floating point number IEEE754
| 8022 | 1F56 | [6 empty] | Output C update phase | RW | float | 4 | 2 | Floating point number IEEE754
| 8024 | 1F58 | [6 empty] | Output phase disable | RW | float | 4 | 2 | Floating point number IEEE754
| 8026 | 1F5A | [6 empty] | Output A phase disable | RW | float | 4 | 2 | Floating point number IEEE754
| 8028 | 1F5C | [6 empty] | Output B phase disable | RW | float | 4 | 2 | Floating point number IEEE754
| 8030 | 1F5E | [6 empty] | Output C phase disable | RW | float | 4 | 2 | Floating point number IEEE754
| 8032 | 1F60 | [6 empty] | Max CSC gain | RW | float | 4 | 2 | Floating point number IEEE754
| 8034 | 1F62 | [6 empty] | Output A max CSC gain | RW | float | 4 | 2 | Floating point number IEEE754
| 8036 | 1F64 | [6 empty] | Output B max CSC gain | RW | float | 4 | 2 | Floating point number IEEE754
| 8038 | 1F66 | [6 empty] | Output C max CSC gain | RW | float | 4 | 2 | Floating point number IEEE754
| 8048 | 1F70 | x |  |  | x |  |  | Continuous self calibration | RW | bool
| 8049 | 1F71 | x |  |  | x |  |  | Output A continuous self calibration | RW | bool
| 8050 | 1F72 | x |  |  | x |  |  | Output B continuous self calibration | RW | bool
| 8051 | 1F73 | x |  |  | x |  |  | Output C continuous self calibration | RW | bool
| 8052 | 1F74 | x |  |  | x |  |  | Fault on saturation | RW | bool
| 8053 | 1F75 | x |  |  | x |  |  | Output A fault on saturation | RW | bool
| 8054 | 1F76 | x |  |  | x |  |  | Output B fault on saturation | RW | bool
| 8055 | 1F77 | x |  |  | x |  |  | Output C fault on saturation | RW | bool
SCPI | 64000 | FA00 | [6 empty] | SCPI Write/query | RW | char | 246 | 123 | ASCII | MEASure:VOLTage:DC:NC#? | 64000 - 65536 (SCPI genérico)
| 64256 | FB00 | [6 empty] | SCPI Command last answer |  |  | 1024 | 512 | ASCII | 0.000,0.000,0.000,0.000
| 64769 | FD01 | x |  |  | x |  |  | SCPI Char 16 endianess | RW | bool |  |  | Coils : Endianess | OFF= little; ON= Inverted
| 64770 | FD02 | x |  |  | x |  |  | SCPI Response next page | RW | bool |  |  | Coils : Next Page | ON=next, self clear